## Slide 1: Upscaling Basic Sanitation for the Urban Poor (UBSUP)
Preparation of final design Technical Drawings Section View

## Slide 2: Content
Questions you might to ask yourself:
What is the context of this session?
What has to be considered during the preparation of the cross-section drawing?

## Slide 3: What is the context of this session?
The SafiSan Toolkit
This session

## Slide 4: Baseline data collection – Existing levels
Take levels at the following locations (along water flow line):
  Level of the final effluent discharge point (flooding level)
  Ground levels where different treatment modules will be located (outlets)
  Existing ground level where the RB will be located (outlet)
  Existing ground level at gate
► To determine in the BoQs the volumes for excavation and refilling (landscaping)

## Slide 5: Baseline existing levels: water flow line
VFCW
VFCW
SDRB
ABR
ST
RB/BT
Storage
CA
Water Flow line (main treatment line)
Water Flow line (SDRB drainage)

## Slide 6: Baseline - existing levels
VFCW
VFCW
SDRB
ABR
ST
RB/BT
Storage
CA
1
Example:
1: 1400.000m (final discharge point)
2: 1400.500m (inspection chamber)
3: 1401.000m (VFCW outlet channel)
4: 1402.000m (ABR/BT outlet pipe)
5: 1403.000m (ST outlet pipe)
6: 1404.000m (RB/BT outlet pipe)
7: 1402.000m (SDRB outlet pipe)
2
3
4
5
6
7

## Slide 7: Design – required minimum levels
VFCW
VFCW
SDRB
ABR
ST
RB/BT
Storage
CA
1
Example:
1: 1400.00m (existing flooding level)
2: 1400.20m (Δd=20m, 1% slope)
3: 1400.40m (Δd=20m, 1% slope)
4: 1401.45m (Δh=0.97m within VFCW + Δd=8m, 1% slope in feeding pipe)
5: 1401.52 (Δd=7m, 1% slope)
6: 1402.54 (Δh=1.02m within ABR/BT)
7: 1402.63 (Δd=9m, 1% slope)
8: 1402.73 (Δh=0.10m within ST)
9: 1402.77 (Δd=4m, 1% slope)
10: 1402.58 (Δd=4m, 1% slope, based on ABR inlet)
2
3
5
6
9
7
8
10
4

## Slide 8: Design – cross-section drawing - A
1400.00
20m, 1%
20m, 1%
1400.20
1400.40
Drainage channel

## Slide 9: Design – cross-section drawing - A
1400.40
8m, 1%
0.97m
1401.45
Drainage channel
Feeding pipe
Bypass pipe

## Slide 10: Design – cross-section drawing - A
1401.45
7m, 1%
1401.52
1402.54
1.02m

## Slide 11: Design – cross-section drawing - A
9m, 1%
1402.54
1402.63
0.1m
1402.73

## Slide 12: Design – cross-section drawing - A
4m, 1%
1402.73
1402.77

## Slide 13: Design – cross-section drawing - A
Total level difference for FS/WW stream: 1402.77-1400.00=2.77m

## Slide 14: Design – cross-section drawing - B
4m, 1%
1402.54
1402.58

## Slide 15: Design – BoQ
The cost for excavation can be calculated based on
  The required levels of the modules
  The existing ground level
pipe
pipe
VFCW
pipe
ABR
ST
pipe
pipe

## Slide 16: Do you have any questions, remarks or suggestions?