## Slide 1: Upscaling Basic Sanitation for the Urban Poor (UBSUP)
Construction of DTFs DO´s & DON´Ts

## Slide 2: Content
Questions you might to ask yourself:
What is the context of this session?
What are general considerations & directions for the construction of a DTF?
What are specific DO´s & DON´Ts for the construction of the different treatment modules and auxiliary works?
Which safety measures are relevant during construction?

## Slide 3: What is the context of this session?
The SafiSan Toolkit
This session

## Slide 4
Objective: To make you understand the DTF concept
Receiving Bay & Balancing Tank
Settler
ABR
Constructed Wetland
Sludge Drying Bed
Co-composting Area
TREATMENT MODULES

## Slide 5
Objective: To make you understand the DTF concept
AUXILIARY WORKS
Inspection Chambers
Operator / Storage Building
Landscaping
Gate & Fence

## Slide 6: General considerations & directions

## Slide 7: Why is it required to put so much effort on a simple construction work?
DTF looks like simple concrete structure but the construction reflexes the complex design, which considers
          Bio-chemical criteria
          Hydraulic criteria
Construction quality is of utmost importance to ensure that the DTF run as designed (or at all) and operate sustainably
  Even small leakages lead to environmental pollution and health risks for operators / neighbours
  Even small errors in levels can lead to clogging, wrong retention times and overflowing

## Slide 8: Which instructions do apply?
The Company Supervisor and the Contractor are responsible to take care that all works are implemented
  State-of-the-art (materials, equipment, technologies)
  Reliable (honest, in-time, dedicated)
  According to technical drawings (i.e. structural)
  According to technical specifications outlined in the bid document
  According to the information provided in the BoQ

## Slide 9: Which sequence of works is recommended?
Works shall be implemented in a logical sequence, not by treatment module, to
  Ensure good construction quality
  Reduce logistical efforts
  Reduce costs related to logistics
  Approval of works shall be done in the same order as implementation of works

## Slide 10: Which sequence of works is recommended?
Mark total site and treatment modules with cornerstones
Clear site, incl. removal of vegetation
Set temporary benchmark (survey mark) for the entire project time
Excavate all modules and do required landscaping
Build foundations and ground slabs for all modules, incl. proper compacting and blending
Build walls for all modules (incl. inspection boxes)

## Slide 11: Which sequence of works is recommended?
Do all piping (inside modules, connecting, drainage, bypass)
Build cover slabs for all modules, incl. manholes
Do water-tight plastering and proper curing
Test system on water tightness
Fill SDRB and VFCW with filter materials and plantation
Test system on operation
Do fencing, final landscaping and construction of access roads, fence and gate

## Slide 12: Which sequence of works is recommended?
Construction of ground slabs requires a big amount of Reinforced Concrete Cement (RCC)
Quality of mortar is crucial for structural stability and water tightness
Contractor is supposed to use a concrete mixer to ensure proper quality
Constructing all required ground slabs at once avoids bringing the concrete mixer to the construction site various times
Example: Construction of ground slabs and foundations

## Slide 13: What about access to and within the site
Access to the construction site and the possibility to manoeuvre within the site is required for:
  Trucks delivering bulk materials: (i) cement, sand and aggregate for mortar (ii) metal bars for reinforcement (iii) gravel for filling the wetland and sludge drying bed (iv) raw water for testing on water tightness / operation
  Machinery: (i) concrete mixer (ii) compactors (iii) excavator (iv) bulldozer, etc

## Slide 14: What about access to and within the site?
  It might be best to start with modules that are located further away from the access point to the DTF site
Access / space must be considered when establishing the final detailed work programme

## Slide 15: How are materials stored to avoid damage?
An elevated and roofed shed is required to store:
  Cement to protect from rain and flooding (risk of hardening)
  Metal bars and mesh (reinforcement) to protect from rain and flooding (risk of corrosion)
  Metal pipes (vent pipes, hand rails for receiving bay) to protect from rain and flooding (risk of corrosion)
  Bituminous felt damp-proof course, damp-proof membrane and PE liner to protect from sunlight (UV radiation destroys structure of plastics)
  uPVC and HDPE pipes to protect from sunlight (UV radiation destroys structure of plastics)

## Slide 16: How are materials stored to avoid damage?
A horizontal storage surface required to store:
  Metal pipes (vent pipes, hand rails for receiving bay) to avoid deformation
  uPVC pipes to avoid risk of deformation
Timber wedge required in between
  Metal pipes to avoid risk of scratching
  uPVC pipes to avoid risk of scratching
  Security and measures against theft required

## Slide 17: How is the benchmark set?
Levels are crucial to avoid non-performance of the DTF
The benchmark is therefore essential and needs to fulfil the following requirements:
  Does not change during the entire project duration in height or location
  Protected against obstruction, damage and unintended / accidental relocation
  Visible from all points of the construction side (if not possible it must be temporarily transferred during work)

## Slide 18: Excavation, backfilling, compacting?
Before constructing foundations and ground slabs, excavation and proper compacting of the underground is essential to:
  Reduce subsequent settlement under working loads
  Increase the shear strength of the soil
  Reduce voids, making it more difficult for water to pass the soil

## Slide 19: Excavation?
Excavation:
  Appropriate depth depends on local soil conditions (e.g. removal of black cotton soil until a hard bed is reached)
  In case of underground modules (i.e. settler and ABR) it is likely that hard bed is reached with the depth of the modules
  In case of structures on ground level further excavation might be required for proper anchoring of the structures

## Slide 20: Backfilling & compacting?
Backfilling
  With approved fill material (either excavated soil or imported filler) in layers of 150mm and compacting until a Maximum Dry Density (MDD) of 95% is reached (compaction test)
  With a layer of 200mm approved hardcore
  Blinding with final material of 25mm thickness
Final compacting of top layer

## Slide 21: Which mortar is to be used?
A proper concrete mixture is essential to ensure structural stability and water tightness
  Ensure that sufficient amount of cement is used Blinding: C15 (1:3:6) Other concrete works: C20 (1:1.5:3)
  Ensure the concrete mix is workable, which allows correct placement and consolidation
  Use a concrete mixer to ensure perfect blending
  Ensure the optimum desired quality of the hardened concrete is met to improve water tightness, wear resistance, and strength

## Slide 22: Which mortar is to be used?
  Avoid too much water; the quality of concrete mainly depends on the water to cement ratio; the mix should be a stiff as possible
  Use the largest aggregate practicable
  Use the optimum ratio of fine to coarse aggregate
  Ensure proper compacting of blinding and concrete ground / roof slabs to ensure water tightness and structural stability
    By default, a compacting machine must be used (a porker vibrator is adequate for this type of works)

## Slide 23: What about reinforcement?
Crucial to support the structural stability of ground / roof slabs and walls
To be done according to structural drawings and BoQ
The following materials are to be used:
  Metal bars for the (i) strip footing of the ground slab (below walls) and (ii) reinforcement of the cover slab
  BRC mesh for the (i) ground slab and (ii) cover slab
Improper reinforcement, e.g. to save material, is not acceptable and the Supervisor and Contractor must be held responsible for any variations from the technical specifications

## Slide 24: What about water tightness?
Crucial for all modules (above or underground) to avoid environmental pollution and groundwater contamination
Design includes various construction elements to ensure tightness
  Bituminous felt damp-proof course laid under the strip footing
  Damp-proof membrane (Gauge 500) laid under the entire ground slab
  Internal and external plastering with water proof cement mortar

## Slide 25: Why is horizontal construction important?
Ensure that ground slabs of all modules are built horizontally to guarantee an equal distribution of
  Loads
  Settled sludge
Ensured by using a levelling machine and/or tube level

## Slide 26: Why is curing so important?
Important due to hot climate conditions and extensive sunlight exposition
Proper curing can be ensured by:
  A minimum of 7 days of curing
  Only after 21 days the maximum strength will be derived
  Freshly cast concrete must be protected against sunlight, drying and evaporation
  Frequent watering may be required to keep the concrete moist

## Slide 27: What is to be considered during backfilling?
Backfilling with soil (after plastering and curing) poses the risk that the soil pressure damages / destroys walls (cracks)
In order to avoid cracks it is recommended to:
  Fill tanks with water during backfilling to compensate soil pressure from outside with water pressure from inside
  Fill water gradually into the tanks while the excavation is backfilled with soil

## Slide 28: How is water-tightness checked?
Crucial to avoid environmental / groundwater pollution
Required quantities:
  A total of 130m3 raw water (borehole or river) are required for the RB/BT + ST + ABR (ABR outlet plugged)
  For Wetland and Sludge Drying Bed (without gravel, outlets plugged) approx. 200m3 are required in each case
  Water can be reused (e.g. pumped from wetland to sludge drying bed)
  For ST and ABR all chambers must be filled simultaneously to avoid unbalanced pressure forces (cracks / collapse)

## Slide 29: How is water-tightness checked?
  Procedure to check tightness:
  Mark maximum water level (e.g. with chalk)
  Wait for 8 hours
  If the water level decreased the Contractor needs to roughen and re-plaster the walls with water-tight mortar (otherwise no completion certificate given)
  Contractor and Construction Supervisor are responsible to ensure that all modules are water tight

## Slide 30: Piping: Which quality of pipes is required?
  Contractor and Supervisor must ensure that pipes with adequate diameter, material and thickness are purchased / used, as outlined in the structural drawings and schedule of materials
  DN 150 class 41 uPVC (pressure) pipe (e.g. main wastewater / bypass pipes between RB/BT and ST)
  DN 100 class 41 uPVC (pressure) pipe (e.g. main wastewater / bypass pipes between after ST, pipes within ST and ABR, drainage pipes)
  DN 50 HDPE (pressure) pipe (VFCW distribution system)
  DN 100 galvanized iron (GI) pipes (air vents, overflows of inspection chambers)

## Slide 31: Piping: Which slope is required?
  DTF usually run purely on gravity
  Ensure a minimum slope in the pipe network (min. 1%)
  Determine the required slope between two points (e.g. outlet of ST and inlet of ABR) by:
  Measure the horizontal distance between both points with a measuring tape (the levels are fixed as per design, related to benchmark)
  Determine the vertical level difference with a tube level / levelling machine
  Calculate the available slope and confirm that it is >1%
10m
0.2m
s=0.2m/10m=0.02=2%

## Slide 32: Piping: How are the pipes laid?
  Underground pipes (connecting / bypass pipes) must withstand certain loads, i.e. if exhauster trucks pass above
  Place pipes on proper sand or gravel bedding (grain size max. 5mm) to prevent breaking
  Principal arrangement of a trench for buried pipes, incl. bedding and backfill:

## Slide 33: Piping: How are the pipes joined?
  Join pipes tightly to avoid leakage (pollution)
  Fitting includes the following work steps – especially in case of ST/ABR distribution pipes this is important to ensure correct length
  Measure and cut
  Prime
  Dry fit
  Glue (special for PVC pipes, applied on both pipes that are to be joined)
  Push and twist
  Use a lever rod and a timber wedge when connecting pipes to avoid that pipes get damaged

## Slide 34: What is the importance of levels?
  DTF is supposed to run on gravity (considered during site selection)
  To avoid hydraulic problems, the following is essential:
  Ensure required levels of slabs and pipes
  Avoid any deviation as even small can lead to clogging and overflowing
  The Contractor and Supervisor need to ensure that all levels are kept:
  Absolute levels of the treatment modules, particularly of the outlet pipes
  Required level differences within the treatment modules
  Regular checks are required during:
  Excavation
  Construction of ground slabs and ground bottoms
  Installation of pipes (i.e. outlet pipes of modules)

## Slide 35: Receiving Bay & Balancing Tank (RB/BT)

## Slide 36: Access to the RB/BT?
  The level depends on the levels of the Settler (1% slope)
  Depending on the existing ground level excavation or backfilling might be required
  Provide a vertical distance between the ground level and the DN 100 inlet pipes of min. 80 cm to connect the truck to the hose
  Build the parking area horizontally to ensure that exhausters can be emptied by gravity entirely
0% slope

## Slide 37: Screens and cleaning channels?
  Ensure that screens are exactly built and installed as per spec´s to avoid clogging during operations and facilitate cleaning:
  Coarse Screen fabricated using GMS bars with diameter of 20 mm
  Spacing between screen bars of 40 mm
  Hinge on top to swing open for easier cleaning

## Slide 38: Screens and cleaning channels?
  Ensure that the concrete U-shape cleaning / drainage channels are built according to the technical specifications:
  300 mm wide to avoid clogging
  Leading to the solid waste chamber to allow for removal of collected solid waste with a shovel or rake

## Slide 39: Water tightness?
  RB/BT is constructed above ground; leaks would result in groundwater contamination, pollution of the surroundings, smell, attraction of flies, carriers of diseases (health risk to operators)
  Build tanks absolutely water-tight:
  Plaster walls properly with a water proof cement mortar (incl. plastic additive) - internally and externally

## Slide 40: Settler (ST)

## Slide 41: Water tightness?
  ST is first treatment step, hence treats untreated faecal sludge
  High risk of groundwater pollution as built underground
  Build ST 100% water-tight:
  Lay felt damp-proof course under the strip footing
  Lay damp-proof membrane (Gauge 50) under the entire ground slab
  Plaster internally and externally with water proof cement mortar (incl. plastic additive)
  Do proper curing of plastering
  Test on water tightness and re-plaster if required

## Slide 42: Connections between chambers?
  First and second ST chambers need to be connected properly
  Allow water flow from the first into the second chamber through three openings that are located below the water level
  Allow for gas exchange through openings located above the water level; forgetting might result in cracks or even bursting as only one ventilation pipe exists

## Slide 43: Ventilation?
  Generated biogas needs to be released to avoid an increase in gas pressure that would result in cracks or even bursts
  Hence one ventilation pipe required (chambers interconnected)
  Built in anti-corrosive GI metal
  Covered with a 90 degrees GI bend (rainwater)
  Mosquito wire gauze (insects)
  Extents at least 2 metres above the cover slab (toxic for operator, risk of explosion)

## Slide 44: Manholes?
  Lots of faecal sludge settles (primary treatment) in the ST and is to be removed regularly by exhauster trucks through manholes:
  Two manholes in first chamber (one above the inlet pipe, one close to the separation wall)
  One manhole in second chamber (above the outlet pipe)
  Located centrally on the slab to allow access to pipes for cleaning
  Standard manholes to be used: 600mm x 450mm air-tight plastic manhole covers, placed into a plastic frame

## Slide 45: Anaerobic Baffle Reactor (ABR)

## Slide 46: Distribution channel & inlet pipes?
  ABR has two separated parallel treatment lines that should treat the same quantity; hence perfect distribution is required
  To ensure water distribution over the entire width a distribution channel is needed
  Channel follows an inspection box equipped with two outlet pipes
  Water is distributed over the entire width as the outlet pipes are slightly elevated above the ground slab of the channel

## Slide 47: Distribution channel & inlet pipes?
  Assure that the water flows equally through all pipes
  Make sure that all outlet pipes are exactly at the same level
  Otherwise the water would only flow through the lowest pipe
Entire treatment line useless
Entire treatment line useless & unequal distribution in other line

## Slide 48: Distribution channel & inlet pipes?
  Ensure that all pipes are constructed exactly at the same level
  2 outlet pipes of inlet box
  6 outlet pipes of the distribution channel
  Mark the exact location (bottom of pipe) before installing pipes
  Use a levelling machine or at least a level tube for marking levels

## Slide 49: Connection pipes inside ABR?
  Mark exact levels at walls before installation
  Determine levels with levelling machine / tube level (not distance from slab as slab might not be horizontal)

## Slide 50: Connection pipes inside ABR?
  Water level is determined by the level of the outlet pipe (bottom of pipe); hence 1,850mm above the ground slab
  Install inlet pipe 150mm higher than the outlet pipe to ensure a hydraulic gradient
  Install inner connection pipes 150mm below the outlet pipe; hence below water level

## Slide 51: Connection pipes inside ABR?
  Six DN100 uPVC inlet pipes per line; hence 36 pipes in total
  Reach to the bottom to a distance of 150mm above ground slab
  Not be too short to ensure good mixture of wastewater with sludge that is accumulating at the bottom
  Not be too long to avoid clogging
  Fixed to the walls with clamps to avoid moving and breaking
  Upper ends of the pipes must protrude the water level

## Slide 52: Connection pipes inside ABR?
  Cut down-flow pipes at the lower end in an angle of 45 degree
  Ensure that the outlet of the pipes is facing the chamber, not the wall
  Consider that pipes are to be joined inside the T-pipes, which reduces the length of the pipes after installation

## Slide 53: Water tightness?
  Provide a damp-proof course to avoid groundwater pollution
  Lay felt damp-proof course under the strip footing
  Lay damp-proof membrane under the ground slab
  Plaster internally and externally with water proof cement mortar (incl. plastic additive)
  Cure walls over the next seven days

## Slide 54: Ventilation?
  Methane needs to be released to avoid cracks or even bursts
  As only one ventilation pipe is foreseen, all 12 chambers (2 lines) are interconnected to allow gas exchange
  Built in anti-corrosive GI metal
  Covered with a 90 degrees GI bend (rainwater)
  Mosquito wire gauze (insects)
  Extents at least 2 metres above the cover slab

## Slide 55: Manholes?
  Needs to be de-sludged regularly by exhausters through manholes:
  Place in cover slab on top of each of the 12 chambers
  Locate centrally to allow access to the inlet pipes (cleaning)
  Use standard manholes (to be lifted by one person) : 600mm x 450mm air-tight plastic manhole covers, placed into a plastic frame

## Slide 56: Siphon?
  Siphon is intended to load the subsequent wetland intermittently
  Proper functioning is crucial for the performance of the entire system
  Works purely hydraulically
  Dimensions and location determine discharge interval, volume, time, flow velocity, etc.

## Slide 57: Siphon?
  Follow the technical specifications laid out in the structural drawings very carefully

## Slide 58: Testing of siphon?
  Test siphon on full functionality before approval is given
  Test when the entire DTF is tested on water tightness (significant quantity of clear water is required)
  Load ABR with clear water (chambers in parallel to avoid cracks)
  Water level in the first chamber rises to about 350mm before the siphon starts draining water from the first tank to the second tank
  Drainage process will stop automatically after approx 4 minutes
  Water level in the first chamber reduces during the drainage interval to approx. 100mm
  Process takes place 15 - 18 times per day
  Inform DTF Flying Squad during testing and convey results

## Slide 59: Electrical wiring?
  Install electrical wires only if the siphon needs to be replaced by a submerged pump (decided with WSTF during site selection / design adaptation)
  In that case the balancing tank needs to be adapted as only one chamber (pump sump) would be required
  If pumping is required:
  Install electrical wires in a cable channel underground
  Don´t forget to lay a pulling wire into the cable channel
  Pull the electrical cable through the channel by means of the pulling wire

## Slide 60: Vertical Flow Constructed Wetland (VFCW)

## Slide 61: Slope of ground bottom and drainage pipes?
  Water trickles through the filter media
  Soakage is drained from the ground bottom towards a collection channel that is running in between the two parallel filter beds
  Lay drainage pipes in a slope of 0.5% towards the collection channel to ensure gravity-based flow / avoid clogging

## Slide 62: Slope of ground bottom and drainage pipes?
  Construct the bottom of the filter beds with the same gradient (0,5%) to ensure the required slope within the pipe network:
  Create gradient when constructing the clay laver below the filter bed and the PE liner
  Place the PVC drainage pipes on top of the PE liner
  Contractor and the Construction Supervisor need to check the 0.5% slope of the bottom before the wetland is filled with gravel

## Slide 63: Water-tight foundation?
  Water-tight bottom layer is important due to large surface area of the filter beds (prevent water losses and groundwater pollution):
  Compacted soil (if required after backfilling with suitable soil)
  Clay layer of 100mm thickness
  PE liner of 1.5mm thickness

## Slide 64: Installation of PE liner?
  The following working steps are required for welding of PE liners
  Install PE sheets, overlapping by 5 to 10 cm
  Prepare and heat weld contact area
  Join sheets that are to be connected under welding pressure (either single or double welding seem)
  Do controlled cooling of the welding seems under continued pressure
  Refinish the welding seems
  Inspect the welding seems on water tightness (optically, with scribing iron, test with blowing, pressure or vacuum test)
  Correct seems by repeated welding (where required)

## Slide 65: Installation of PE liner?
  Fill the filter beds with clear water and monitor the water level on tightness before filling with gravel
  Use a specialized Contractor for laying and welding:
  Required experience and know-how
  Electrical welding machine for wedge / hot air welding of PE liners
    e.g. companies specialised on the construction of fish/shrimp ponds, aquacultures and landfills

## Slide 66: Installation of drainage pipes?
  Drainage pipes pass the PE liner before they end in the channel
  Joints between pipes and PE liner must be water-tight
  Connect inner part of drainage pipe (running at the bottom of the filter bed) with the outer part (connecting the drainage pipe with the collection channel) with a pipe duct (pipe flange)
  Flange can be either made of PVC or anti-corrosive metal
  Use adapters to connect pipes with commercially available / customized flange
  Place PE liner in between two flanges and screw together

## Slide 67: Installation of drainage pipes?
  If flanges are not available or feasible, PVC pipes can be connected to the PE liner by welding and use of brackets
  Cut a hole into the PE liner where the pipe is supposed to pass the liner
  Extent the PE liner by welding additional sheets of PE to it
  Put the extended PE liner over the pipe and fixe it with brackets

## Slide 68: Installation of drainage pipes?
  If neither pipe ducts nor the welding / brackets are available or feasible for any reasons, the connections could be sealed using bitumen or duct tape
  This solution is however less durable
  Finally the Company and the Contractor should decide which technology they want to use.
  It just must be assured that the connection is water tight

## Slide 69: Shape of drainage pipes?
  Use commercially available DN100 PVC drainage pipe (perforated/slotted)
  Are ready-made pipes not available the Contractor might be allowed by the Construction Supervisor to drill holes into regular PVC pipe
  Size of the holes / slots must be smaller than 8mm to avoid clogging

## Slide 70: Mixture of filter materials?
  Ensure that mixtures are uniform to avoid clogging (large, medium, small pebbles are distributed equally in the entire volume)
  De-mixing can occur due to individual weights and forms of the different corn sizes during transport to the site (e.g. through vibration of the lorry) or unloading (i.e. in case of tipper trucks)
  Larger particles will lay on the bottom-centre of a heap
  Assure that de-mixing is minimized by
  Careful driving with the lorry to minimize vibrations
  Careful unloading, preferably manually instead of tipping
  Conscious loading of the filter beds

## Slide 71: Mixture of filter materials?
  Re-mixing after transport and unloading might be required
  The Construction Supervisor needs to confirm to the Contractor that the gravel is ready to be loaded into the filter beds

## Slide 72: Installation of filter materials?
  Filter bed to be filled in 3 separate(d) layers
  Drainage: coarse gravel to (i) ensure an equal distribution of filtrate over the entire bottom area, (ii) to ensure that no small gravel enters the drainage pipes
  Filter: finer gravel to provide a large surface area for bacteria to attach, (ii) to act like a mechanical filter, (iii) to provide a large surface for roots to attach
  Surface: coarse gravel (i) to avoid clogging of the filter media by allowing the water to infiltrate quickly into the filter beds, (ii) to facilitate an equal distribution of the loaded wastewater over the entire surface area

## Slide 73: Installation of filter materials?
  Take care of arranging the different filter layers according to the technical drawings
  otherwise the treatment performance will deteriorate
  to avoid clogging
  Procured gravel is often dirty (dust and fine sand / abrasion), or dust/particles occur from unloading
  Clean gravel with water to flush off dust and sand before filling of the filter beds

## Slide 74: Installation of filter materials?
  Sharp edged material / quarry stones
  can lead to damage of the PE foil sealing (no water-tightness)
  may impede the development and growth of the vegetation
  Ensure that only round gravel (e.g. river pebbles) is used (no quarry stones)
  especially for the drainage layer

## Slide 75: Installation of filter materials?
  Ensure that the filter material is not compacted during incorporation
  No (very limited) stepping on the filled material
  In order to avoid soil compaction, filling is to take place from supporting planks

## Slide 76: Distribution pipes?
  DN50 HDPE perforated pipes to be used as distribution pipes
  laid in parallel
  laid in 1m distance
  laid within the surface layer of the filter beds
  slightly covered by the 8/16 gravel to avoid / reduce smell, mosquito breeding, sunlight exposition, damage during O&M
8/16 gravel
DN50 HDPE pipes
4/8 gravel

## Slide 77: Distribution pipes?
  Lay pipes in a slight slope of 0.5% towards the end of the filter beds to ensure that the water is distributed over the entire surface
  Create slope during placement of the pipes
  Use perforated pipes with holes of 10mm diameter
  Place holes every 1 running meter

## Slide 78: Planting of filter beds?
  Common reed (phragmites australis) is the most common plant used
  Reed can be planted as clumps, individual rhizomes or as seedlings
  Clumps can be planted all year round, preferably during the rainy season; 2 clumps per m2
  Rhizomes are planted when the rhizomes have one or two 10 - 60 cm shoots; 4 – 6 rhizomes per m2
  Seedlings (developed in greenhouses) are planted if they show the start of rhizomes; easier to plant than pieces of rhizome and grow lushly in the first season; 3 - 5 seedlings per m2 are sufficient

## Slide 79: Planting of filter beds?
  Avoid soil compaction by planting from supporting planks
  Provide plant beds immediately following construction with a freeboard of 20 -30 cm (distance from the bed surface to the upper edge of the sealing)
  Fix edge of the sealing (PE liner) with gravel to avoid destruction / removal of the PE liner and for visual reasons
  Water plants during construction, commissioning and first months of operation (if no rain) until they have reached a height of some 50cm

## Slide 80: Drainage / bypass channel?
  Soakage of the filter beds is routed via drainage pipes (0.5% slope) into drainage channel
  Running in between the two filter beds
  Construct the channel with a slope of 1% to avoid clogging
  Used as bypass (if both beds are closed down for any reason)
  Channel is covered by precast concrete covers
  Y10 lifting handle rings to provide easy access for cleaning
  Do not exceed 600mm x 600mm x 50mm for weight reasons

## Slide 81: Effluent pipe?
  Inspection chamber is placed at the end of the drainage channel
  From this chamber the effluent shall be routed through a DN100 uPVC pipe towards the receiving water body (i.e. a river or trench)
  Lay pipe with at least 0.5% slope (1% if topography allows)
  Place inspection chambers every 25 meters to allow access to the pipe system for cleaning in case of any clogging
  Use standard inspection chambers with the dimension of 1200mm x 825mm, covered with 600mm x 450mm x 50mm PVC covers

## Slide 82: Sludge Drying Reed Bed (SDRB)

## Slide 83: Level?
  Level depends on the level of a nearby treatment module
  Ensure a slope of min 0.5% in the connecting pipe
  Backfill if required as per existing ground level
  A parking area / ramp might be required
  Horizontal to ensure that exhausters can be emptied by gravity
  Height must ensure that the truck outlet is higher than the surface of the SDRB
0% slope

## Slide 84: Slope of ground and drainage pipes?
  Soakage is drained from the ground towards a collection pipe
  Provide ≥0.5% slope in the drainage pipes to allow for gravity flow
  Build ground of the drying chambers with a 5% slope towards the drainage pipe to allow easy collection of the soakage
  Create 5% slope during construction of clay layer
  Check slope before PE liner and drainage pipes are installed

## Slide 85: Water tightness?
  Similar to the VFCW, seal the bottom water-tight
  Same working steps as for VFCW: (i) compact soil, (ii) construct a 100mm thick clay layer, (iii) install a 1.5mm PE liner
  Same installation of PE liner as for VFCW: (i) overlapping installation of PE sheets, (ii) preparation and joining of sheets by overlap welding, (iii) cooling and refinishing of welding seems, (iv) inspection on water-tightness, and (v) corrections as required
  Again, an experienced Contractor with electrical welding machine PE liners required
  Install the PE liner of SDRB at same time as for VFCW
  Ensure a water-tight passage of PVC pipes through the PE liner (flange; welding & bracket)

## Slide 86: Mixture and installation of filter material?
  Fill different filter layers as required to avoid clogging
  Use round gravel (e.g. river pebbles) for the drainage / rock layer to avoid that PE liner gets damaged by sharp edged stones
  Avoid compaction of filter material during filling (use planks)
  Wash filter material before loading

## Slide 87: Plantation?
  Similar to plantation of VFCW

## Slide 88: Co-composting Area (CA)

## Slide 89: Level?
  Construct slightly above ground level to avoid that rainwater runoff flows into the shed during heavy rainfall
  Elevation of at least 30cm above the surrounding ground level
  Ensure level by means of adequate landscaping during construction
  Build drainage channels around the shed to reduce the required elevation (if preferred)

## Slide 90: Drainage channels?
  Leachate might (!) be generated during the composting process and should be drained to avoid nuisances
  Construct longitudinal drainage channel in the centre of the CA
  Provide a slope of 1% towards the intended drainage side
  Create channel and its slope during the plastering of the platform
  Provide a slope of 1% towards the drainage channel in the platform during plastering of the ground slab The leachate can be infiltrated into the ground by means of a small pit filled with gravel

## Slide 91: Supporting columns for roof?
  Roof has a considerable weight (steel truss, roofing sheets)
  Ensure good construction quality for the supporting columns
  Proper quality of square hollow section (SHS) columns, metal plates and bolts (anti-corrosive)
  Proper cement mixture (C20) for concrete pillars
  Proper use of formworks during construction
  Proper installation of the bolts into the concrete pillars to allow for easy installation of the metal plate
  Proper fixing of the screw nuts on the bolts, avoiding any kind of friction that could result in damaging the concrete pillars

## Slide 92: Supporting columns for roof?
  Good construction quality is crucial to ensure that the roof resists rough weather conditions such as heavy rain or storms

## Slide 93: Chambers & Pipes

## Slide 94: Types of inspection chambers?
  Two kinds of inspection chambers are foreseen for the DTF:
  Standard chamber to a depth of 1m below ground level
  Standard chamber to a depth of more than 1 meter

## Slide 95: Location of inspection chambers?
  Inspection chambers are generally located:
  Every 25 meters to provide access to buried pipes
  Where the flow direction of pipes changes, i.e. in case of bypasses

## Slide 96: Plugging of pipes?
  Pipes, particularly bypasses, need to be plugged
  Use regular plastic plugs / end caps for plugging the PVC pipes:
  End cap that is pressed outside the normal end of a pipe
  Plug that is pressed inside the socket (recommended as the pipe end has a rubber sealing; hence the plugging is water-tight)
  Fix plugs permanently to the inspection box with a rustproof, stainless steel chain to avoid theft

## Slide 97: Plugging of pipes?
  Assure that pipes are placed in a way that the sockets are accessible in order being able to close pipes with plugs from inside
  Ensure that the pipe end finishes with the plastering of the inspection box (it is not required to build any kind of channel)
  If the sockets are not accessible in an inspection chamber, the pipe cannot be plugged

## Slide 98: Flow regulation at Receiving Bay?
  Main flow into the system is regulated to ensure a steady flow and to avoid peaks
  Place a penstock sliding valve at the outlet pipe of the Balancing Tank
  The inspection chamber also hosts outlets to the settler (bottom of chamber), a bypass (slightly elevated), as well as an overflow (on top of chamber)

## Slide 99: Flow regulation upstream Wetland?
  Flow is diverted between the intermittently operating filter beds
  A volume-wise flow regulation is not required
  Place PVC ballcock valves into the DN50 HDPE feeding pipes leading to the filter beds
  Plug the bypass pipe in an attached dry chamber

## Slide 100: Flow regulation upstream Wetland?
Ballcock valve
Arrangement of 2 ballcock valves and outlet to bypass (to be plugged in second chamber)

## Slide 101: Covers?
  Build all covers as per technical specifications:
  Inspection chambers
  inlet/outlet boxes of treatment modules
  Distribution channels
  Balancing tanks and treatment modules
  Ensure that the manhole covers can be lifted easily by one person (DTF operator)
  Fix PVC covers permanently to the inspection box with a rustproof, stainless steel chain to avoid theft
  Equip covers with a moveable ring handle to avoid risk of stumbling or use standard covers with 2 small halls for hooking it up with e.g. screwdriver

## Slide 102: Operator / Storage Building

## Slide 103: Water supply?
  Connect the building to water supply
  O&M purposes (cleaning of equipment)
  Personal hygiene (water flush toilet, hand washing)
  Install a water tap outside the building for cleaning boots, tools, etc. before entering the building
  Supply fresh water either by
  Pipe network
  Rainwater harvesting
  Borehole or a well
  Cistern filled occasionally by lorries

## Slide 104: Energy supply?
  If possible by any means, supply the building with electricity
  Lighting
  O&M
  This can be done by
  Connection to a nearby power grid
  Equipping the building with a solar system
  Side note: energy supply is required anyhow if the decision was taken during the site selection and design adaptation phase to install a pump instead of a siphon to load the wetland system

## Slide 105: Drainage?
  Drain and treat generated wastewater, as the building is equipped with a wash basin and toilet
  Connect the building by gravity to a DTF treatment module, i.e. the receiving bay, settler or ABR

## Slide 106: Auxiliary Works

## Slide 107: Final landscaping & drainage?
  A general risk of flooding exists during rain events (dilution, reduced treatment capacity)
  Ensure that all modules are not prone to flooding during rain
  Co-composting area is independent
  Build the co-composting area above the existing / or final ground level
  Avoid flooding of the other modules (levels depend on receiving water body) by final landscaping and proper drainage
  Ensure that cover slabs of settler, ABR, inspection chambers extent at least 20cm above final ground level (freeboard)
  Ensure that barriers of the wetland system and sludge drying beds extent at least 30cm above final ground level (freeboard)
  Flatten the site to allow access to all modules for trucks and SaniGo

## Slide 108: Fence?
  Take care to locate the fence appropriately and as per design
  Ensure sufficient distance between treatment modules and fence (incl. space that trucks can access all modules for O&M)
  Avoid access to the site for unauthorised persons to avoid damages, theft and personal injuries; particularly children
  Ensure that the fence is not installed outside the assigned land to avoid legal problems
  Ensure that the fence is located at solid grounds, or ensure proper foundation, in order to ensure structural stability
  Follow the technical specifications to ensure structural stability

## Slide 109: Gate?
  Location of the gate is determined during the final design
  Ensure during construction that the gate is constructed in a way that guarantees:
  Easy access of exhauster trucks to the receiving bay, having in mind required manoeuvring
  Easy access of exhauster trucks and SaniGo to the gate from outer roads

## Slide 110: Health and Safety

## Slide 111: Basic rules for safety?
  Tidy construction site
  Keep passages clear all time to avoid stumbling, stepping into nails
  Pile materials safely; stacks should not be too high
  Beware of floor openings and ensure that they are covered
  Remove waste as soon as possible
  Safety Measures
  Ensure that dangerous part of machines have been installed with a guard
  Keep vigilant all the time and watch out for moving equipment
  Before you use any electrical tool, check the condition of its cables
  Avoid dragging electric cables on the ground or allowing the cables to come into contact with water

## Slide 112: Basic rules for safety?
  Personal safety
  Wear protective equipment
  Do not drink or take drugs while working
  Pay attention to personal hygiene
  Do not play in the workplace
  Report to your supervisor immediately if you notice any unsafe condition

## Slide 113: Emergency Response?
  Have a good understanding of your working environment
  When evacuation is required in an emergency, you should keep calm and find out
  What dangerous situation the alarm refers to
  The routes for evacuation
  The safe place that you should go to as designated by the company

## Slide 114: Emergency Response?
  If an accident happen despite safety precautions it is important to:
  Keep calm
  Seek help immediately
  Accompany the injured person
  Assist in the immediate rescue work as far as possible
  Do not try to move the injured person unless it is really necessary

## Slide 115: Emergency Response?
  When a fire breaks out, you should remember:
  Put out the fire with a fire extinguisher if it is a small fire
  If the blaze is out of control, do not try to extinguish the fire on your own; call the Fire Services Department, or the police (999) right away

## Slide 116: HEALTH & SAFETY EXAMPLES?
  Excavations
  Use safe access for ingress and egress
  Do not pile soil or any other materials at the edge of an excavation
  Make sure that a trench is securely shored before working in it
  Gas welding & flame cutting (i.e. for roof of composing area)
  Wear personal protective equipment (i.e. safety glasses)
  Place fire extinguishers within reach
  Keep gas cylinders upright and secure it against overturning
  If gas leakage is detected, report it to your supervisor immediately

## Slide 117: HEALTH & SAFETY EXAMPLES?
  Fire risk
  Always keep the workplace clean and tidy
  Handle machinery and tools that may generate sparks or heat carefully
  Do not smoke or use naked flames in any area where flammable and explosive substances are stored
  Know where fire extinguishers are located and how they are used
  Know the place of assembly for fire evacuation

## Slide 118: HEALTH & SAFETY EXAMPLES?
  Waste disposal
  Dispose all wastes and unwanted materials must be disposed of at a designated place
  Separate disposal of chemical or inflammable wastes
  Do not leave planks with nails on passageways
  Eye protection
  A small fragment entering an eye may cause serious consequences
  Wear suitable eye protectors when there is a risk of eye injury, such as in concrete breaking
  Take proper care of the eye protectors provided to you; replace damaged eye protectors immediately

## Slide 119: HEALTH & SAFETY EXAMPLES?
  Noise
  Wear ear protectors in areas with high noise levels
  Do not reuse disposable ear plugs
  Clean ear protectors regularly
  Personal Protective Equipment
  Wear gloves when handling or contacting chemicals
  Wear a mask when working in a dusty environment
  Wear eye and ear protectors whenever necessary
  Wear safety shoes to prevent foot injury
  Wear a safety helmet on a construction site

## Slide 120: HEALTH & SAFETY EXAMPLES?
  First Aid
  Ensure that a first aid kit is available at the construction site
  Identify in advance a colleague who is trained in first aid procedures
  Manual handling
  Avoid manual handling operations as far as possible
  Lift an object with a correct posture (e.g. straight back)
  Put on gloves to protect your hands from cuts, scratch or puncture
  Wear safety boots or shoes to prevent injury to toes by heavy falling objects
  Seek assistance from someone in lifting a load if necessary

## Slide 121: Do you have any questions, remarks or suggestions?