## Table 1,2,3
Table 1: Water Demand 1)
Designation |  | Unit | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
Population
| Total | No | 86109 | 88288.8493 | 90523.8816 | 92815.4936 | 95165.1178 | 97574.2228 | 100044.3142 | 102576.9361 | 105173.6712 | 107836.1427 | 110566.0146 | 113364.9933 | 116234.8281 | 119177.3128 | 122194.2864 | 125287.6348 | 128459.2913 | 131711.2382 | 135045.5082 | 138464.1853 | 141969.4061
| - Existing Areas | No | 86109 | 88288.8493 | 90523.8816 | 92815.4936 | 95165.1178 | 97574.2228 | 100044.3142 | 102576.9361 | 105173.6712 | 107836.1427 | 110566.0146 | 113364.9933 | 116234.8281 | 119177.3128 | 122194.2864 | 125287.6348 | 128459.2913 | 131711.2382 | 135045.5082 | 138464.1853 | 141969.4061
| - New Development Area | No | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - New Towns and Villages | No | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total new population | No | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - Growth rate | %/a | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315 | 2.5315
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - Population served | % | 54 | 56.2 | 58.4 | 60.6 | 62.8 | 65 | 70 | 75 | 80 | 85 | 90 | 91.6 | 93.2 | 94.8 | 96.4 | 98 | 98 | 98 | 98 | 98 | 98
| - Domestic | No | 46498.86 | 49618.3333 | 52865.9468 | 56246.1891 | 59763.694 | 63417.2448 | 70031.02 | 76932.702 | 84138.937 | 91660.7213 | 99509.4132 | 103842.3339 | 108330.8598 | 112980.0925 | 117795.2921 | 122781.8821 | 125890.1055 | 129077.0135 | 132344.5981 | 135694.9016 | 139130.018
Specific Water demand
| - Domestic | l/cap/day | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7
| increase | %/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| billing ratio | % | 62.5 | 70 | 77.5 | 85 | 92.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| actual consumption | l/cap/day | 56.0625 | 62.79 | 69.5175 | 76.245 | 82.9725 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7 | 89.7
Total Water Consumption
| - Domestic | mill. m3/a | 1.5224 | 1.6245 | 1.7309 | 1.8415 | 1.9567 | 2.0763 | 2.2929 | 2.5188 | 2.7548 | 3.001 | 3.258 | 3.3998 | 3.5468 | 3.699 | 3.8567 | 4.0199 | 4.1217 | 4.226 | 4.333 | 4.4427 | 4.5552
| - Commercial/Industry | mill. m3/a | 0.15224 | 0.16245 | 0.17309 | 0.18415 | 0.19567 | 0.20763 | 0.22929 | 0.25188 | 0.27548 | 0.3001 | 0.3258 | 0.33998 | 0.35468 | 0.3699 | 0.38567 | 0.40199 | 0.41217 | 0.4226 | 0.4333 | 0.44427 | 0.45552
| - Institutional 2) | mill. m3/a | 0.28004 | 0.29883 | 0.31839 | 0.33874 | 0.35993 | 0.38193 | 0.42176 | 0.46333 | 0.50673 | 0.55203 | 0.5993 | 0.62539 | 0.65242 | 0.68042 | 0.70942 | 0.73945 | 0.75817 | 0.77737 | 0.79705 | 0.81722 | 0.83791
Total Net Demand |  | mill. m3/a | 1.9547 | 2.0858 | 2.2223 | 2.3644 | 2.5123 | 2.6659 | 2.9439 | 3.234 | 3.537 | 3.8531 | 4.1831 | 4.3652 | 4.5539 | 4.7493 | 4.9518 | 5.1614 | 5.292 | 5.426 | 5.5634 | 5.7042 | 5.8486
| - Commercial/Industry | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| - Institutional | l/cap/d | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
| UFW 3) | % | 73.8 | 65.04 | 56.28 | 47.52 | 38.76 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | mill. m3/a | 1.4426 | 1.3566 | 1.2507 | 1.1236 | 0.97376 | 0.79976 | 0.88317 | 0.97021 | 1.0611 | 1.1559 | 1.2549 | 1.3096 | 1.3662 | 1.4248 | 1.4855 | 1.5484 | 1.5876 | 1.6278 | 1.669 | 1.7113 | 1.7546
Gross Demand |  | mill. m3/a | 3.3972 | 3.4424 | 3.4731 | 3.488 | 3.4861 | 3.4656 | 3.8271 | 4.2042 | 4.598 | 5.0091 | 5.438 | 5.6748 | 5.9201 | 6.1742 | 6.4373 | 6.7098 | 6.8797 | 7.0538 | 7.2324 | 7.4155 | 7.6032
1) aasumed to reflect about actual situation |  |  |  | 2) including schools. Health and public services | [5 empty] | 3) including 5% treatment works losses
Table 3: Connections
Designation |  | Unit | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
Households |  |  | 6369.7068 | 6797.032 | 7241.9105 | 7704.9574 | 8186.8074 | 10569.5408 | 11671.8367 | 12822.117 | 14023.1562 | 15276.7869 | 19901.8826 | 20768.4668 | 21666.172 | 22596.0185 | 23559.0584 | 24556.3764 | 25178.0211 | 25815.4027 | 26468.9196 | 27138.9803 | 27826.0036
| < 10 m3/month | No | 1719.8208 | 1835.1986 | 1955.3158 | 2080.3385 | 2210.438 | 2853.776 | 3151.3959 | 3461.9716 | 3786.2522 | 4124.7325 | 5373.5083 | 5607.486 | 5849.8664 | 6100.925 | 6360.9458 | 6630.2216 | 6798.0657 | 6970.1587 | 7146.6083 | 7327.5247 | 7513.021
| 11 - 20 m3/month | No | 2993.7622 | 3194.605 | 3403.6979 | 3621.33 | 3847.7995 | 4967.6842 | 5485.7632 | 6026.395 | 6590.8834 | 7180.0898 | 9353.8848 | 9761.1794 | 10183.1008 | 10620.1287 | 11072.7575 | 11541.4969 | 11833.6699 | 12133.2393 | 12440.3922 | 12755.3207 | 13078.2217
| > 20 m3/month | No | 1592.4267 | 1699.258 | 1810.4776 | 1926.2394 | 2046.7018 | 2642.3852 | 2917.9592 | 3205.5293 | 3505.789 | 3819.1967 | 4975.4707 | 5192.1167 | 5416.543 | 5649.0046 | 5889.7646 | 6139.0941 | 6294.5053 | 6453.8507 | 6617.2299 | 6784.7451 | 6956.5009
| Total Household connections | No | 6306.0098 | 6729.0616 | 7169.4914 | 7627.9078 | 8104.9393 | 10463.8454 | 11555.1183 | 12693.8958 | 13882.9246 | 15124.019 | 19702.8638 | 20560.7821 | 21449.5102 | 22370.0583 | 23323.4678 | 24310.8127 | 24926.2409 | 25557.2487 | 26204.2304 | 26867.5905 | 27547.7436
|  |  | 0 | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.245 | 0.44 | 0.635 | 0.83 | 1.025 | 1.22 | 1.415 | 1.61 | 1.805 | 2 | 2.0667 | 2.1333 | 2.2 | 2.2667 | 2.3333
|  |  | 1 | 0.81 | 0.62 | 0.43 | 0.24 | 0.05 | 0.245 | 0.44 | 0.635 | 0.83 | 1.025 | 1.22 | 1.415 | 1.61 | 1.805 | 2 | 2.0667 | 2.1333 | 2.2 | 2.2667 | 2.3333
Commercial/Industry |  | No | 260 | 260.026 | 260.078 | 260.156 | 260.2601 | 260.3902 | 261.0282 | 262.1767 | 263.8415 | 266.0314 | 268.7582 | 272.0371 | 275.8864 | 280.3282 | 285.3881 | 291.0959 | 297.1118 | 303.4502 | 310.1261 | 317.1557 | 324.556
Institutions |  | No | 500 | 504.05 | 507.1751 | 509.356 | 510.5784 | 510.8337 | 512.0852 | 514.3384 | 517.6045 | 521.9006 | 527.2501 | 533.6825 | 541.2341 | 549.948 | 559.8746 | 571.0721 | 582.8742 | 595.3089 | 608.4057 | 622.1962 | 636.7141
Total Connections
| Beginning | No | 7066.0098 | 7493.1376 | 7936.7445 | 8397.4198 | 8875.7778 | 11235.0693 | 12328.2317 | 13470.411 | 14664.3706 | 15911.951 | 20498.8721 | 21366.5017 | 22266.6308 | 23200.3345 | 24168.7305 | 25172.9806 | 25806.2269 | 26456.0078 | 27122.7622 | 27806.9424 | 28509.0136
| Additional | No | 0 | 443.6069 | 460.6753 | 478.358 | 2359.2915 | 1093.1624 | 1142.1792 | 1193.9596 | 1247.5804 | 4586.9211 | 867.6296 | 900.1291 | 933.7037 | 968.396 | 1004.2501 | 633.2464 | 649.7808 | 666.7544 | 684.1801 | 702.0713 | 720.4416
| Ending | No | 7066.0098 | 7936.7445 | 8397.4198 | 8875.7778 | 11235.0693 | 12328.2317 | 13470.411 | 14664.3706 | 15911.951 | 20498.8721 | 21366.5017 | 22266.6308 | 23200.3345 | 24168.7305 | 25172.9806 | 25806.2269 | 26456.0078 | 27122.7622 | 27806.9424 | 28509.0136 | 29229.4552
Table 2 : Water per User Group 1)
Designation |  | Unit | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
Domestic
| 0 - 10 m3 | mill. m3/a | 0.41105 | 0.43862 | 0.46733 | 0.49721 | 0.52831 | 0.5606 | 0.61907 | 0.68008 | 0.74378 | 0.81027 | 0.87966 | 0.91796 | 0.95764 | 0.99874 | 1.0413 | 1.0854 | 1.1129 | 1.141 | 1.1699 | 1.1995 | 1.2299
| 11 - 20 m3 | mill. m3/a | 0.71553 | 0.76353 | 0.8135 | 0.86552 | 0.91965 | 0.97587 | 1.0776 | 1.1838 | 1.2947 | 1.4105 | 1.5313 | 1.5979 | 1.667 | 1.7385 | 1.8126 | 1.8894 | 1.9372 | 1.9862 | 2.0365 | 2.0881 | 2.1409
| 0 - 10 m3 | mill. m3/a | 0.025148 | 0.026835 | 0.028591 | 0.030419 | 0.032322 | 0.041729 | 0.04608 | 0.050622 | 0.055363 | 0.060313 | 0.078573 | 0.081994 | 0.085538 | 0.089209 | 0.093011 | 0.096949 | 0.099403 | 0.10192 | 0.1045 | 0.10714 | 0.10986
| 11 - 20 m3 | mill. m3/a | 0.69038 | 0.73669 | 0.78491 | 0.8351 | 0.88732 | 0.93414 | 1.0316 | 1.1332 | 1.2394 | 1.3502 | 1.4527 | 1.5159 | 1.5815 | 1.6493 | 1.7196 | 1.7924 | 1.8378 | 1.8843 | 1.932 | 1.9809 | 2.0311
| > 20 m3 | mill. m3/a | 0.3806 | 0.40613 | 0.43271 | 0.46038 | 0.48917 | 0.51908 | 0.57321 | 0.6297 | 0.68869 | 0.75025 | 0.8145 | 0.84996 | 0.8867 | 0.92476 | 0.96417 | 1.005 | 1.0304 | 1.0565 | 1.0833 | 1.1107 | 1.1388
| 0 - 10 m3 | mill. m3/a | 0.014714 | 0.015701 | 0.016729 | 0.017798 | 0.018912 | 0.024416 | 0.026962 | 0.029619 | 0.032393 | 0.035289 | 0.045973 | 0.047975 | 0.050049 | 0.052197 | 0.054421 | 0.056725 | 0.058161 | 0.059634 | 0.061143 | 0.062691 | 0.064278
| 11 - 20 m3 | mill. m3/a | 0.0057327 | 0.0061173 | 0.0065177 | 0.0069345 | 0.0073681 | 0.0095126 | 0.010505 | 0.01154 | 0.012621 | 0.013749 | 0.017912 | 0.018692 | 0.0195 | 0.020336 | 0.021203 | 0.022101 | 0.02266 | 0.023234 | 0.023822 | 0.024425 | 0.025043
| > 20 m3 | mill. m3/a | 0.36015 | 0.38431 | 0.40947 | 0.43565 | 0.46289 | 0.48515 | 0.53575 | 0.58854 | 0.64367 | 0.70122 | 0.75061 | 0.7833 | 0.81715 | 0.85222 | 0.88854 | 0.92616 | 0.9496 | 0.97364 | 0.99829 | 1.0236 | 1.0495
Commercial / Industry |  | mill. m3/a | 0.15224 | 0.16245 | 0.17309 | 0.18415 | 0.19567 | 0.20763 | 0.22929 | 0.25188 | 0.27548 | 0.3001 | 0.3258 | 0.33998 | 0.35468 | 0.3699 | 0.38567 | 0.40199 | 0.41217 | 0.4226 | 0.4333 | 0.44427 | 0.45552
Institutions 2) |  | mill. m3/a | 0.28004 | 0.29883 | 0.31839 | 0.33874 | 0.35993 | 0.38193 | 0.42176 | 0.46333 | 0.50673 | 0.55203 | 0.5993 | 0.62539 | 0.65242 | 0.68042 | 0.70942 | 0.73945 | 0.75817 | 0.77737 | 0.79705 | 0.81722 | 0.83791
| Total | mill. m3/a | 1.9395 | 2.0696 | 2.205 | 2.346 | 2.4927 | 2.6451 | 2.921 | 3.2088 | 3.5094 | 3.8231 | 4.1505 | 4.3312 | 4.5184 | 4.7124 | 4.9132 | 5.1212 | 5.2508 | 5.3838 | 5.52 | 5.6598 | 5.8031
1) based on current water consumption
2) including municipalities and institutions such as hospitals and schools
|  |  | -0.015224 | -0.016245 | -0.017309 | -0.018415 | -0.019567 | -0.020763 | -0.022929 | -0.025188 | -0.027548 | -0.03001 | -0.03258 | -0.033998 | -0.035468 | -0.03699 | -0.038567 | -0.040199 | -0.041217 | -0.04226 | -0.04333 | -0.044427 | -0.045552

## Table 4
|  |  |  | Table 4: Water Tariffs | [6 empty] | 12.25 | % real increases per year
|  |  |  | Designation |  | Unit | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
Domestic
[5 empty] | 0 - 10 m3 1) | Ksh/m3 | 20 | 20 | 22.45 | 25.2001 | 28.2871 | 31.7523 | 35.642 | 40.0081 | 44.209 | 48.8509 | 53.9803 | 59.6482 | 65.9112 | 72.8319 | 80.4793 | 88.9296 | 98.2672 | 108.5853 | 119.9867 | 132.5853 | 146.5068
[5 empty] | 11 - 20 m3 | Ksh/m3 | 25 | 25 | 28.0625 | 31.5002 | 35.3589 | 39.6904 | 44.5525 | 50.0101 | 55.2612 | 61.0636 | 67.4753 | 74.5602 | 82.3891 | 91.0399 | 100.5991 | 111.162 | 122.834 | 135.7316 | 149.9834 | 165.7316 | 183.1335
[5 empty] | > 20 m3 | Ksh/m3 | 30 | 30 | 33.675 | 37.8002 | 42.4307 | 47.6285 | 53.463 | 60.0122 | 66.3135 | 73.2764 | 80.9704 | 89.4723 | 98.8669 | 109.2479 | 120.7189 | 133.3944 | 147.4008 | 162.8779 | 179.9801 | 198.878 | 219.7602
|  |  |  | Commercial 2) |  | Ksh/m3 | 33.75 | 33.75 | 37.8844 | 42.5252 | 47.7345 | 53.582 | 60.1458 | 67.5137 | 74.6026 | 82.4359 | 91.0917 | 100.6563 | 111.2252 | 122.9039 | 135.8088 | 150.0687 | 165.8259 | 183.2376 | 202.4776 | 223.7377 | 247.2302
Institutions
[5 empty] | - General 2) | Ksh/m3 | 45 | 45 | 50.5125 | 56.7003 | 63.6461 | 71.4427 | 80.1944 | 90.0183 | 99.4702 | 109.9145 | 121.4556 | 134.2084 | 148.3003 | 163.8718 | 181.0784 | 200.0916 | 221.1012 | 244.3168 | 269.9701 | 298.317 | 329.6402
[5 empty] | - Schools | Ksh/m3 | 20 | 20 | 22.45 | 25.2001 | 28.2871 | 31.7523 | 35.642 | 40.0081 | 44.209 | 48.8509 | 53.9803 | 59.6482 | 65.9112 | 72.8319 | 80.4793 | 88.9296 | 98.2672 | 108.5853 | 119.9867 | 132.5853 | 146.5068
[5 empty] | - Churches/Mosques | Ksh/m3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Construction |  | Ksh/m3 | 300 | 300 | 336.75 | 378.0019 | 424.3071 | 476.2847 | 534.6296 | 600.1217 | 663.1345 | 732.7636 | 809.7038 | 894.7227 | 988.6686 | 1092.4788 | 1207.1891 | 1333.9439 | 1474.008 | 1628.7789 | 1799.8007 | 1988.7797 | 2197.6016
|  |  |  | Industry 2) |  | Ksh/m3 | 85 | 85 | 95.4125 | 107.1005 | 120.2203 | 134.9473 | 151.4784 | 170.0345 | 187.8881 | 207.6164 | 229.4161 | 253.5048 | 280.1228 | 309.5357 | 342.0369 | 377.9508 | 417.6356 | 461.4874 | 509.9435 | 563.4876 | 622.6538
|  |  |  | Consumer Registration Fee |  | Ksh/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meter rent households |  |  |  | Connection Fees |  | Ksh/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 - 10 | 0.27 | 50 | 13.5 | Meter rent
11 - 50 | 0.47 | 50 | 23.5 |  | domestic 2) | Ksh/con. | 49.5 | 49.5 | 55.5637 | 62.3703 | 70.0107 | 78.587 | 88.2139 | 99.0201 | 109.4172 | 120.906 | 133.6011 | 147.6292 | 163.1303 | 180.259 | 199.1862 | 220.1007 | 243.2113 | 268.7485 | 296.9671 | 328.1487 | 362.6043
> 50 | 0.25 | 50 | 12.5 |  | commercial/industry | Ksh/con. | 800 | 800 | 898 | 1008.005 | 1131.4856 | 1270.0926 | 1425.6789 | 1600.3246 | 1768.3587 | 1954.0364 | 2159.2102 | 2385.9272 | 2636.4496 | 2913.2768 | 3219.1709 | 3557.1838 | 3930.6881 | 4343.4104 | 4799.4685 | 5303.4127 | 5860.271
|  |  | 49.5 |  | institutions | Ksh/con. | 450 | 450 | 505.125 | 567.0028 | 636.4607 | 714.4271 | 801.9444 | 900.1826 | 994.7018 | 1099.1455 | 1214.5557 | 1342.0841 | 1483.0029 | 1638.7182 | 1810.7836 | 2000.9159 | 2211.0121 | 2443.1683 | 2699.701 | 2983.1696 | 3296.4024
Customers Deposit
[5 empty] | domestic | Ksh/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | commercial/industry | Ksh/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | institutions | Ksh/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Exchange rate (Ksh/€) 3) |  |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
|  |  |  | Domestic |  | Unit | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
[5 empty] | 0 - 10 m3 | €/m3 | 0.22727 | 0.22727 | 0.25511 | 0.28637 | 0.32144 | 0.36082 | 0.40502 | 0.45464 | 0.50237 | 0.55512 | 0.61341 | 0.67782 | 0.74899 | 0.82764 | 0.91454 | 1.0106 | 1.1167 | 1.2339 | 1.3635 | 1.5067 | 1.6648
[5 empty] | 11 - 20 m3 | €/m3 | 0.28409 | 0.28409 | 0.31889 | 0.35796 | 0.40181 | 0.45103 | 0.50628 | 0.5683 | 0.62797 | 0.6939 | 0.76676 | 0.84728 | 0.93624 | 1.0345 | 1.1432 | 1.2632 | 1.3958 | 1.5424 | 1.7044 | 1.8833 | 2.0811
[5 empty] | > 20 m3 | €/m3 | 0.34091 | 0.34091 | 0.38267 | 0.42955 | 0.48217 | 0.54123 | 0.60753 | 0.68196 | 0.75356 | 0.83269 | 0.92012 | 1.0167 | 1.1235 | 1.2415 | 1.3718 | 1.5158 | 1.675 | 1.8509 | 2.0452 | 2.26 | 2.4973
|  |  |  | Commercial |  | €/m3 | 0.38352 | 0.38352 | 0.4305 | 0.48324 | 0.54244 | 0.60889 | 0.68348 | 0.7672 | 0.84776 | 0.93677 | 1.0351 | 1.1438 | 1.2639 | 1.3966 | 1.5433 | 1.7053 | 1.8844 | 2.0822 | 2.3009 | 2.5425 | 2.8094
Institutions
|  |  |  | - General |  | €/m3 | 0.51136 | 0.51136 | 0.57401 | 0.64432 | 0.72325 | 0.81185 | 0.9113 | 1.0229 | 1.1303 | 1.249 | 1.3802 | 1.5251 | 1.6852 | 1.8622 | 2.0577 | 2.2738 | 2.5125 | 2.7763 | 3.0678 | 3.39 | 3.7459
|  |  |  | - Schools / Hospitals |  | €/m3 | 0.22727 | 0.22727 | 0.25511 | 0.28637 | 0.32144 | 0.36082 | 0.40502 | 0.45464 | 0.50237 | 0.55512 | 0.61341 | 0.67782 | 0.74899 | 0.82764 | 0.91454 | 1.0106 | 1.1167 | 1.2339 | 1.3635 | 1.5067 | 1.6648
|  |  |  | - Chuches/Mosques |  | €/m3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Construction |  | €/m3 | 3.4091 | 3.4091 | 3.8267 | 4.2955 | 4.8217 | 5.4123 | 6.0753 | 6.8196 | 7.5356 | 8.3269 | 9.2012 | 10.1673 | 11.2349 | 12.4145 | 13.7181 | 15.1585 | 16.7501 | 18.5089 | 20.4523 | 22.5998 | 24.9727
|  |  |  | Industry |  | €/m3 | 0.96591 | 0.96591 | 1.0842 | 1.2171 | 1.3661 | 1.5335 | 1.7213 | 1.9322 | 2.1351 | 2.3593 | 2.607 | 2.8807 | 3.1832 | 3.5175 | 3.8868 | 4.2949 | 4.7459 | 5.2442 | 5.7948 | 6.4033 | 7.0756
|  |  |  | Consumer Registration Fee |  | €/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Connection Fees |  | €/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meter rent
[5 empty] | domestic | €/con. | 0.5625 | 0.5625 | 0.63141 | 0.70875 | 0.79558 | 0.89303 | 1.0024 | 1.1252 | 1.2434 | 1.3739 | 1.5182 | 1.6776 | 1.8538 | 2.0484 | 2.2635 | 2.5011 | 2.7638 | 3.054 | 3.3746 | 3.729 | 4.1205
[5 empty] | commercial/industry | €/con. | 9.0909 | 9.0909 | 10.2045 | 11.4546 | 12.8578 | 14.4329 | 16.2009 | 18.1855 | 20.095 | 22.205 | 24.5365 | 27.1128 | 29.9597 | 33.1054 | 36.5815 | 40.4225 | 44.6669 | 49.3569 | 54.5394 | 60.2661 | 66.594
[5 empty] | institutions | €/con. | 5.1136 | 5.1136 | 5.7401 | 6.4432 | 7.2325 | 8.1185 | 9.113 | 10.2293 | 11.3034 | 12.4903 | 13.8018 | 15.251 | 16.8523 | 18.6218 | 20.5771 | 22.7377 | 25.1251 | 27.7633 | 30.6784 | 33.8997 | 37.4591
Customers Deposit
[5 empty] | domestic | €/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | commercial/industry | €/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | institutions | €/con. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 1) | tariffs in 2006 correspond to present tariffication | [5 empty] | 2) average rates of different consumption groups
|  |  |  | 3) | for details see Chapter "Introduction" in the report

## Table 5,6,7
TABLE 5 : Existing Infrastructure 1)
|  | Unit |  | Investment |  |  | Tax | other | Total |  |  |  |  | Quote part |  | Economic
Designation | Unit | Cost | Quantity | foreign | local | Total | 2) | taxes, fees | Cost | Civil | M&E | Mobile | Services | local 3) | foreign | life
|  | 000 € |  | 000 € | 000 € | 000 € | 000 € | 000 € | Mill. € |  |  | equipm. |  | % | % | years
Preparatory works
Feasibility study | ls | 15 | 1 | 10.5 | 4.5 | 15 | 0 | 0 | 0.015 |  |  |  | 0.015 | 30 | 70 | 15
Leak detection | ls | 20 | 1 | 12.4 | 7.6 | 20 | 0 | 0 | 0.02 |  |  |  | 0.02 | 38 | 62 | 15
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 30 | 70 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 100 | 15
Sub Total |  |  |  | 22.9 | 12.1 | 35 | 0 | 0 | 0.035 | 0 | 0 | 0 | 0.035 | 34.5714 | 65.4286
Raw Water Intake
Pumping stations | ls | 39.773 | 1 | 15.9092 | 23.8638 | 39.773 | 0 | 0 | 0.039773 | 0.021875 | 0.017898 |  |  | 60 | 40 | 40
Rising mains | ls | 12.039 | 1 | 10.8351 | 1.2039 | 12.039 | 0 | 0 | 0.012039 | 0.0096312 | 0.0024078 |  |  | 10 | 90 | 15
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 80 | 20 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 80 | 20 | 40
Sub Total |  |  |  | 26.7443 | 25.0677 | 51.812 | 0 | 0 | 0.051812 | 0.031506 | 0.020306 | 0 | 0 | 48.382 | 51.618
Boreholes
BH 1 | ls | 4.773 | 1 | 2.1479 | 2.6251 | 4.773 | 0 | 0 | 0.004773 | 0.004773 |  |  |  | 55 | 45 | 40
BH 2 | ls | 5.648 | 1 | 4.236 | 1.412 | 5.648 | 0 | 0 | 0.005648 | 0.005648 |  |  |  | 25 | 75 | 40
BH 3 | ls | 8.273 | 1 | 5.3774 | 2.8956 | 8.273 | 0 | 0 | 0.008273 | 0.008273 |  |  |  | 35 | 65
Service road | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 70 | 30 | 15
Sub Total |  |  |  | 11.7613 | 6.9327 | 18.694 | 0 | 0 | 0.018694 | 0.018694 | 0 | 0 | 0 | 37.0852 | 62.9148
Water Treatment Plant
Pumping stations | ls | 79.545 | 1 | 11.9317 | 67.6132 | 79.545 | 0 | 0 | 0.079545 | 0.04375 | 0.035795 |  |  | 85 | 15 | 40
Buildings | ls | 170.455 | 1 | 76.7048 | 93.7503 | 170.455 | 0 | 0 | 0.17046 | 0.13636 | 0.034091 |  |  | 55 | 45 | 40
Composite Treatment Units | ls | 936.364 | 1 | 140.4546 | 795.9094 | 936.364 | 0 | 0 | 0.93636 | 0.65545 | 0.28091 |  |  | 85 | 15
Rising mains | ls | 275.644 | 1 | 121.2834 | 154.3606 | 275.644 | 0 | 0 | 0.27564 | 0.19295 | 0.082693 |  |  | 56 | 44
Mobile equipment | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 65 | 35
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 80 | 20
Sub Total |  | 0 |  | 350.3745 | 1111.6335 | 1462.008 | 0 | 0 | 1.462 | 1.0285 | 0.43349 | 0 | 0 | 76.0347 | 23.9653
Sewerage System
Shirere Sewage Treatment Works | ls | 386.364 | 1 | 170.0002 | 216.3638 | 386.364 | 0 | 0 | 0.38636 | 0.19318 | 0.19318 |  |  | 56 | 44 | 15
Kambi Somali Sewage Treatment Works | ls | 85.227 | 1 | 40.909 | 44.318 | 85.227 | 0 | 0 | 0.085227 | 0.042613 | 0.042613 |  |  | 52 | 48
Sewer Network | ls | 507.55 | 1 | 253.775 | 253.775 | 507.55 | 0 | 0 | 0.50755 | 0.35529 | 0.15227 |  |  | 50 | 50
Sub Total |  |  |  | 464.6841 | 514.4569 | 979.141 | 0 | 0 | 0.97914 | 0.59108 | 0.38806 | 0 | 0 | 52.5417 | 47.4583
Storage System
Concrete Tank,Capacity 450 m3 | ls | 30.682 | 1 | 16.8751 | 13.8069 | 30.682 | 0 | 0 | 0.030682 | 0.010739 | 0.019943 |  |  | 45 | 55
Concrete Tank,Capacity 450 m3 | ls | 76.364 | 1 | 42.0002 | 34.3638 | 76.364 | 0 | 0 | 0.076364 | 0.026727 | 0.049637 |  |  | 45 | 55
Elevated Steel Tank, Capacity 90 m3 | ls | 10.227 | 1 | 1.534 | 8.693 | 10.227 | 0 | 0 | 0.010227 | 0.0035795 | 0.0066476 |  |  | 85 | 15
Elevated Steel Tank, Capacity 45 m3 | ls | 5.114 | 1 | 0.7671 | 4.3469 | 5.114 | 0 | 0 | 0.005114 | 0.0017899 | 0.0033241 |  |  | 85 | 15
Capacity 5.000 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 7.500 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 10.000 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 15.000 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 20.000 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 30.000 m3 | piece | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Sub Total |  |  |  | 61.1765 | 61.2105 | 122.387 | 0 | 0 | 0.12239 | 0.042835 | 0.079552 | 0 | 0 | 50.0139 | 49.9861
Distribution Sytem
Primary | ls | 1572.806 | 1 | 550.4821 | 1022.3239 | 1572.806 | 0 | 0 | 1.5728 | 1.5728 |  |  |  | 65 | 35
Secondary | ls | 397.345 | 1 | 139.0708 | 258.2743 | 397.345 | 0 | 0 | 0.39735 | 0.39735 |  |  |  | 65 | 35
Tertiary | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 70 | 30
House connections | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 85 | 15
Sub Total |  |  |  | 689.5528 | 1280.5982 | 1970.151 | 0 | 0 | 1.9702 | 1.9702 | 0 | 0 | 0 | 65 | 35
Services
| ls |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 10 | 90
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 10 | 90
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 10 | 90
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 10 | 90
Sub Total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Land Aquisition | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0
Total |  |  |  | 1627.1935 | 3011.9995 | 4639.193 | 0 | 0 | 4.6392 | 3.6828 | 0.92141 | 0 | 0.035 | 64.9251 | 35.0749
1) 2005 prices | 2) no tax considered
TABLE 6 : Rehabilitation Costs 1)
|  | Unit |  | Investment |  |  | V.A.T. | other | Total |  |  |  |  | Quote part |  | Economic
Designation | Unit | Cost | Quantity | foreign | local | Total | 2) | taxes, fees | Cost | Civil | M&E | Miscell. | Services | local 3) | foreign | life
|  | 000 € |  | 000 € | 000 € | 000 € | 000 € | 000 € | Mill. € |  |  |  |  | % | % | years
Raw Water Intake | [15 empty] | 15
New raw water intake | ls | 30.948 | 1 | 12.3792 | 18.5688 | 30.948 | 0 | 0 | 0.030948 | 0.030948 |  |  |  | 60 | 40
Old raw water intake | ls | 5.903 | 1 | 5.3127 | 0.5903 | 5.903 | 0 | 0 | 0.005903 | 0.005903 |  |  |  | 10 | 90
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 25 | 75
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 100 | 0 | 15
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 90 | 10 | 15
Sub Total |  |  |  | 17.6919 | 19.1591 | 36.851 | 0 | 0 | 0.036851 | 0.036851 | 0 | 0 | 0 | 51.9907 | 48.0093
Boreholes | [15 empty] | 15
Rising mains | ls | 6 | 1 | 2.7 | 3.3 | 6 | 0 | 0 | 0.006 | 0.0042 | 0.0018 |  |  | 55 | 45 | 40
Booster pumps | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25 | 75 | 40
Mechanical and electrical equipment | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 35 | 65
Service road | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 70 | 30
Sub Total |  |  |  | 2.7 | 3.3 | 6 | 0 | 0 | 0.006 | 0.0042 | 0.0018 | 0 | 0 | 55 | 45
Water Treatment Plant
Rehabilitation works | ls | 292.975 | 1 | 43.9462 | 249.0288 | 292.975 | 0 | 0 | 0.29298 | 0.16114 | 0.13184 |  |  | 85 | 15 | 15
Sedimentation tanks | ls | 80.659 | 1 | 36.2966 | 44.3624 | 80.659 | 0 | 0 | 0.080659 | 0.064527 | 0.016132 |  |  | 55 | 45 | 0
Chemical mixing & dosing Units | ls | 22.727 | 1 | 3.4091 | 19.3179 | 22.727 | 0 | 0 | 0.022727 | 0.0090908 | 0.013636 |  |  | 85 | 15
Flocculation Units | ls | 5.682 | 1 | 2.5001 | 3.1819 | 5.682 | 0 | 0 | 0.005682 | 0.0039774 | 0.0017046 |  |  | 56 | 44 | 0
Treated water rising mains | ls | 207.432 | 1 | 72.6012 | 134.8308 | 207.432 | 0 | 0 | 0.20743 | 0.12446 | 0.082973 |  |  | 65 | 35 | 0
Sub Total |  |  |  | 158.7531 | 450.7219 | 609.475 | 0 | 0 | 0.60947 | 0.36319 | 0.24628 | 0 | 0 | 73.9525 | 26.0475
Sewerage System
Sewage Treatment Work | ls | 301.046 | 1 | 132.4602 | 168.5858 | 301.046 | 0 | 0 | 0.30105 | 0.30105 |  |  |  | 56 | 44
Sewer Network | ls | 814.34 | 1 | 390.8832 | 423.4568 | 814.34 | 0 | 0 | 0.81434 |  | 0.81434 |  |  | 52 | 48
Miscellaneous | ls | 67.955 | 1 | 33.9775 | 33.9775 | 67.955 | 0 | 0 | 0.067955 | 0.020387 | 0.047568 |  |  | 50 | 50
Sub Total |  | 0 |  | 557.3209 | 626.0201 | 1183.341 | 0 | 0 | 1.1833 | 0.32143 | 0.86191 | 0 | 0 | 52.9028 | 47.0972
Storage System
Concrete Tank,Capacity 1.120 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 45 | 55 | 0
Concrete Tank,Capacity 450 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 45 | 55
Elevated Steel Tank, Capacity 90 m3 | ls | 11.364 | 1 | 1.7046 | 9.6594 | 11.364 | 0 | 0 | 0.011364 | 0.0073866 | 0.0039774 |  |  | 85 | 15
Elevated Steel Tank, Capacity 45 m3 | ls | 5.682 | 1 | 0.8523 | 4.8297 | 5.682 | 0 | 0 | 0.005682 | 0.0036933 | 0.0019887 |  |  | 85 | 15
Rehabilitation of valves | ls | 5.682 | 1 | 0.8523 | 4.8297 | 5.682 | 0 | 0 | 0.005682 | 0.0036933 | 0.0019887 |  |  | 85 | 15
Capacity 7500 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 10000 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Capacity 15000 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15 | 0
Capacity 20000 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15 | 0
Capacity 30000 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15 | 0
Sub Total |  |  |  | 3.4092 | 19.3188 | 22.728 | 0 | 0 | 0.022728 | 0.014773 | 0.0079548 | 0 | 0 | 85 | 15
Distribution System
General Rehabilitation works | ls | 88.069 | 1 | 30.8241 | 57.2448 | 88.069 | 0 | 0 | 0.088069 | 0.026421 | 0.061648 |  |  | 65 | 35 | 40
Provision of elevated tanks | ls | 49.668 | 1 | 17.3838 | 32.2842 | 49.668 | 0 | 0 | 0.049668 | 0.032284 | 0.017384 |  |  | 65 | 35 | 40
Extension of water & service mains | ls | 428.197 | 1 | 128.4591 | 299.7379 | 428.197 | 0 | 0 | 0.4282 | 0.12846 | 0.29974 |  |  | 70 | 30 | 40
Installation of water meters | ls | 412.5 | 1 | 61.875 | 350.625 | 412.5 | 0 | 0 | 0.4125 | 0.0825 | 0.33 |  |  | 85 | 15
Sub Total |  |  |  | 238.542 | 739.8919 | 978.434 | 0 | 0 | 0.97843 | 0.26966 | 0.70877 | 0 | 0 | 75.62 | 24.38
Control System
Scada system | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 15 | 85 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 10 | 90 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0 | 40
Sub Total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Miscellaneous
3 Pick-ups, Motor bikes | ls | 92.046 | 1 | 82.8414 | 9.2046 | 92.046 | 0 | 0 | 0.092046 |  |  | 0.092046 |  | 10 | 90
Tools & equipment | ls | 142.045 | 1 | 35.5112 | 106.5337 | 142.045 | 0 | 0 | 0.14205 |  |  | 0.14205 |  | 75 | 25 | 40
Billing & GIS software | ls | 40 | 1 | 0 | 40 | 40 | 0 | 0 | 0.04 |  |  | 0.04 |  | 100 | 0 | 40
Preliminaries & general items | ls | 622.183 | 1 | 0 | 622.183 | 622.183 | 0 | 0 | 0.62218 | 0.18665 | 0.43553 |  |  | 100 | 0 | 40
Sub Total |  |  |  | 118.3526 | 777.9214 | 896.274 | 0 | 0 | 0.89627 | 0.18665 | 0.43553 | 0.27409 | 0 | 86.795 | 13.205
Land aquisition | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0
Total |  |  |  | 1096.7699 | 2636.3331 | 3733.103 | 0 | 0 | 3.7331 | 1.1968 | 2.2622 | 0.27409 | 0 | 70.6204 | 29.3796
1) 2005 prices | 2) no tax considered
TABLE 7 : Investment Costs Extension 1)
|  | Unit |  | Investment |  |  | V.A.T. | other | Total |  |  |  |  | Quote part |  | Economic
Designation | Unit | Cost | Quantity | foreign | local | Total | 2) | taxes, fees | Cost | Civil | M&E | Miscell. | Services | local | foreign | life
|  | 000 € |  | 000 € | 000 € | 000 € | 000 € | 000 € | Mill. € |  |  |  |  | % | % | years
Raw Water Intake | [15 empty] | 15
Investments | ls | 411.59 | 1 | 144.0565 | 267.5335 | 411.59 | 0 | 0 | 0.41159 | 0.12348 | 0.28811 |  |  | 65 | 35 | 15
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 65 | 35 | 15
| ls | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 65 | 35 | 15
| ls | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 65 | 35
| ls | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 65 | 35 | 15
Sub Total |  |  |  | 144.0565 | 267.5335 | 411.59 | 0 | 0 | 0.41159 | 0.12348 | 0.28811 | 0 | 0 | 65 | 35 | 15
Boreholes | [15 empty] | 15
General expansion works | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 65 | 35 | 15
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 65 | 35
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 65 | 35
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 65 | 35
Sub Total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 15
Water Treatment Plant | [15 empty] | 0
Civil works | ls | 2663.182 | 1 | 399.4773 | 2263.7047 | 2663.182 | 0 | 0 | 2.6632 | 1.1984 | 1.4648 |  |  | 85 | 15
Mech. & electrical equipment | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 55 | 45 | 0
Energy transm. line + transformer | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Pressure main | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 56 | 44
Sub Total |  |  |  | 399.4773 | 2263.7047 | 2663.182 | 0 | 0 | 2.6632 | 1.1984 | 1.4648 | 0 | 0 | 85 | 15 | 0
Sewerage System
8.500 m3 Treatment & Ancillary works | ls | 2636.932 | 1 | 1160.2501 | 1476.6819 | 2636.932 | 0 | 0 | 2.6369 | 2.6369 | 0 |  |  | 56 | 44
3.500 m3 Treatment & Ancillary works | ls | 1244.886 | 1 | 597.5453 | 647.3407 | 1244.886 | 0 | 0 | 1.2449 | 1.2449 | 0 |  |  | 52 | 48
Sewers | ls | 2591.364 | 1 | 1295.682 | 1295.682 | 2591.364 | 0 | 0 | 2.5914 | 0.77741 | 1.814 |  |  | 50 | 50
Preliminaries & General items | ls | 1294.636 | 1 | 609.7378 | 684.8982 | 1294.636 | 0 | 0 | 1.2946 | 0.64732 | 0.64732 |  |  | 52.9028 | 47.0972
Sub Total |  |  |  | 3663.2152 | 4104.6028 | 7767.818 | 0 | 0 | 7.7678 | 5.3065 | 2.4613 | 0 | 0 | 52.8411 | 47.1589
Storage System | [15 empty] | 0
1000 m3 Storage | ls | 946.364 | 1 | 520.5002 | 425.8638 | 946.364 | 0 | 0 | 0.94636 | 0.61514 | 0.33123 |  |  | 45 | 55 | 0
Concrete Tank,Capacity 450 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 45 | 55 | 0
Elevated Stel Tank, Capacity 90 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Elevated Stel Tank, Capacity 45 m3 | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85 | 15
Sub Total |  |  |  | 520.5002 | 425.8638 | 946.364 | 0 | 0 | 0.94636 | 0.61514 | 0.33123 | 0 | 0 | 45 | 55 | 40
Distribution System | [15 empty] | 40
General expansion works | ls | 5534.99 | 1 | 1937.2465 | 3597.7435 | 5534.99 | 0 | 0 | 5.535 | 5.535 |  |  |  | 65 | 35 | 40
Provision of elevated tanks | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 65 | 35
Extension of water & service mains | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 70 | 30
Installation of water meters | ls | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 85 | 15
Sub Total |  |  |  | 1937.2465 | 3597.7435 | 5534.99 | 0 | 0 | 5.535 | 5.535 | 0 | 0 | 0 | 65 | 35 | 40
Control System | [15 empty] | 40
| ls | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 100 | 40
| ls | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 10 | 90 | 40
| ls | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 100
| ls | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0
Sub Total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100
Miscellaneous | [15 empty] | 40
Preliminaries & General items | ls | 1911.225 | 1 | 477.8062 | 1433.4188 | 1911.225 | 0 | 0 | 1.9112 | 1.9112 |  |  |  | 75 | 25 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 75 | 25 | 40
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 100
| ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 100
Sub Total |  |  |  | 477.8062 | 1433.4188 | 1911.225 | 0 | 0 | 1.9112 | 1.9112 | 0 | 0 | 0 | 75 | 25
Land aquisition | ls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 100 | 0
Total |  |  |  | 7142.3019 | 12092.8671 | 19235.169 | 0 | 0 | 19.2352 | 14.6898 | 4.5454 | 0 | 0 | 62.8685 | 37.1315
1) 1998 prices | 2) no tax considered